## Sheet1
|  | ELEKTRİK İÇ TESİSAT / PANO UYGUNLUK GÖZLE MUAYENE VE TEST RAPORU | [10 empty] | Doküman Adı : |  |  | F.710.01
[13 empty] | Yayın Tarihi : |  |  | 2019-12-16
Sayfa No :
[13 empty] | Revizyon No. : |  |  | 01
[13 empty] | Rapor Tarihi / Rev. : |  |  | 2021-10-16 / 1
[13 empty] | Rapor No : |  |  | TK21-038-02-ET/01 10 /01/ EY
Atalar Mah. Pazar Caddesi No. 48 B Körfez 41780 KOCAELİ Tel:0262.5286255
N=Normally F=Faulty | QUICK TOWER FL.09 DYSON OFFICE | DOĞRUDAN DOKUNMAYA KARŞI KORUMA | [8 empty] | KARŞILIKLI ZARARLI ETKİLERİN ÖNLENMESİ |  | TANIMLAMA |  |  |  | KABLO ve İLETKENLER |  |  | Sismik kontrol | Termal kamera kontrolu varsa İmaj No.
|  | Gerilim altındaki bölümlerin yalıtılması TEMEL YALITIM |  |  | Mahfaza (Pano) |  |  |  | Artık akım anahtarı ile yapılan ilave koruma
No |  | Kablo PVC yalıtım kontrolu | Kablo uç noktası yalıtımı | Kablo ek noktası yalıtımı | IP-XX Sınıfı | Pano dış kapak kilidi | Pano dış kapağı topraklama köprüsü | Pano iç kapağının sadece anahtar veya aletle açılması | AAA / RCD ile Sigorta akımının uyumu | 30mA ve 5.IΔn için 40ms etiket | Elektriksel Olmayan Tes.Yaklaşma ve Diğer Etkilerin Kontrolü | Güvenlik Devre Ayrılması | Şemalar, Talimatlar, Devre Çizimleri ve Kısa Bilgiler | Tehlike İşaretleri ve Diğer Uyarı İşaretleri | Koruma Cihaz ve Terminal Etiket |  | Kablo Yollarının Uygunluğu ve Mekanik Koruma | Kablo Renk Kod Nötr: Mavi Topr: Sarı/ Yeşil | Sıcaklık Etkisine Karşı Koruma | Deprem emniyeti
1 | LIGHTING MAIN DISTR. PANEL | N | N | N | IP-32 | N | N | N | N | -- | N | N | N | N | N |  | N | N | N | N | N
Uygun | [20 empty] | TE#5435-36
CB:Q1:40A,3phases-4poles/ RCD:25A,30mA Relay
2 | ELEC. OUTLETS / MECHANICS MAIN DISTR. PANEL | N | N | N | IP-31 | N | N | N | N | -- | N | N | N | N | N |  | N | N | N | N | N
Uygun | [20 empty] | TE#5437-38
CB:Q2:100A/80A,3phases-4poles/ RCD:25A,30mA Relay
3 | NORMAL ELEC. OUTLETS / UPS MAIN DISTR. PANEL12 | N | F | -- | IP-44 | N | F | -- | -- | -- | F | F | -- | -- | -- |  | F | F | F | -- | --
Uygunsuzluklar Mevcut | [20 empty] | TE#5439-43
CB:Q3:40A,3phases-4poles/ RCD:25A,30mA Relay33
4 | NORMAL ELEC. OUTLETS / UPS MAIN DISTR. PANEL1 | F | F | F | IP-32 | F | F | F | F | F | F | F | F | F | F |  | F | F | F | F | F
Uygunsuzluklar Mevcut | [20 empty] | TE#5439-41
CB:Q3:40A,3phases-4poles/ RCD:25A,30mA Relay1
Note 1: All panels are Compatible of RCD and CB current rate.
Note 2: Toroid is not available but flat 9 electrical room Main Supply Panel has 300 mA RCD for each supply line.
Note 3: Danger signs and other voltage warning signs are posted on the outer cover of panel .
Note 4: Fire Detection / Protection against temperature influence with temperature sensors. / NOT 5
| F.710.01..R01 formu -2- Nüsha Olarak Düzenlenmiştir. İmzasız Formlar Geçersizdir | [8 empty] | N : Normally = Normal F : Faulty = Hatalı -- : Not Available = Yok
[7 empty] | Elektrik Kontrol Uzmanı : | [11 empty] | ONAY :
Note 1: All panels are Compatible of RCD and CB current rate.
Note 2: Toroid is not available but flat 9 electrical room Main Supply Panel has 300 mA RCD for each supply line.
Note 3: Danger signs and other voltage warning signs are posted on the outer cover of panel .
Note 4: Fire Detection / Protection against temperature influence with temperature sensors. / NOT 5
| F.710.01..R01 formu -2- Nüsha Olarak Düzenlenmiştir. İmzasız Formlar Geçersizdir | [8 empty] | N : Normally = Normal F : Faulty = Hatalı -- : Not Available = Yok